## Sheet1
DEC. | HEX | READABLE / | DATA | COEFF. | DEFINITION | INV_11 | INV_33 | UPS_11 | UPS_31 | UPS_33
ADDRESS | ADDRESS | WRITABLE
0 | 0x00 | R / WR | set_V_FLOAT | 10x | battery float charge voltage | NO | NO | YES | YES | YES
1 | 0x01 | R / WR
2 | 0x02 | R / WR | set_V_LOWBAT | 10x | low battery voltage level | YES | YES | YES | YES | YES
3 | 0x03 | R / WR | set_DC_START | 10x | DC voltage low level where INV to RUN again after DC FAIL | YES | YES | YES | YES | YES
4 | 0x04 | R / WR | set_INV_out | 10x | inverter output AC voltage | YES | YES | YES | YES | YES
5 | 0x05 | R / WR | set_F_out | 10x | inverter output frequency (50 or 60 Hz) | YES | YES | YES | YES | YES
6 | 0x06 | R / WR
7 | 0x07 | R / WR | set_I_aku | 10x | battery charge current limit | NO | NO | YES | YES | YES
8 | 0x08 | R / WR
9 | 0x09 | R / WR | set_B_inv | 1x | 1=Nornal LS, 2=Stand-BY, 3=BYPASS-Inhibited, 4=Redundant LS | YES | YES | YES | YES | YES
10 | 0x0a | R / WR
11 | 0x0b | R / WR | set_A_inv | 1x | Automatic RUN condition after fail remove 1=Active, 0=Passive | YES | YES | YES | YES | YES
12 | 0x0c | R / WR
13 | 0x0d | R / WR
14 | 0x0e | R / WR | set_C_inv | 1x | inverter on/off switch "0=OFF, 1=ON" | YES | YES | YES | YES | YES
15 | 0x0f | R / WR | set_C_rec | 1x | Rectifier on/off switch decimal "19=OFF, 3=ON" | NO | NO | YES | YES | YES
16 | 0x10 | R / WR | set_HT_NM_BUS | 1x | currently displayed event number from event history | YES | YES | YES | YES | YES
17 | 0x11 | R / WR
18 | 0x12 | R / WR
19 | 0x13 | R / WR
20 | 0x14 | R / WR | set_DAY | 1x | day of DATE | YES | YES | YES | YES | YES
21 | 0x15 | R / WR | set_MONTH | 1x | month of DATE | YES | YES | YES | YES | YES
22 | 0x16 | R / WR | set_YEAR | 1x | year of DATE | YES | YES | YES | YES | YES
23 | 0x17 | R / WR | set_HOUR | 1x | hour of TIME | YES | YES | YES | YES | YES
24 | 0x18 | R / WR | set_MINUTE | 1x | minute of TIME | YES | YES | YES | YES | YES
25 | 0x19 | R | F_byp | 10x | Bypass frequency | YES | YES | YES | YES | YES
26 | 0x1a | R | V_bat | 10x | Battery_voltage | YES | YES | YES | YES | YES
27 | 0x1b | R | T_internal | 10x | Cabinet Temperature in celcius degree | YES | YES | YES | YES | YES
28 | 0x1c | R | V_byp_L1 | 10x | Bypass Voltage on L1 Phase | YES | YES | YES | YES | YES
29 | 0x1d | R | V_line12 | 10x | GRID Line Voltage between L12 Phase | NO | NO | YES | YES | YES
30 | 0x1e | R | V_inv_L1 | 10x | Inverter Voltage on L1 Phase | YES | YES | YES | YES | YES
31 | 0x1f | R | I_out_L1 | 10x | Output Current on L1 Phase (Bypass or INV) | YES | YES | YES | YES | YES
32 | 0x20 | R | I_rec_L1 | 10x | Rectifier Input Current on L1 Phase | NO | NO | YES | YES | YES
33 | 0x21 | R | V_dcbus | 10x | Inverter DC bus Voltage | YES | YES | YES | YES | YES
34 | 0x22 | R | I_battery | 10x | battery current (signed int16) | NO | NO | YES | YES | YES
35 | 0x23 | R | Fail_code_inv | 1x | INVERTER FAIL CODE (Decimal) | YES | YES | YES | YES | YES
1= IGBT FUSE FAIL
2=MAINTANANCE SW ON, Maintanance Switch activated
3=EPO/RPO ON, Emengent-Remote POWER OFF signal detected
4=DC BUS FAIL, DC Bus has long deviation
5=OUTPUT HIGH/LOW, Inverter Output Voltage has long deviation
6=INTERNAL HIGH TEMP., Termistor detected > 50C inside temp.
7=HEATSINK HIGH TEMP., 70C termostat is activated
8=OVERLOAD, Overload detected from Current Sensor
9=IGBT OVERLOAD, Overload detected from IGBT Saturation
10=INV. DISCONNECTED, Communication Fail
36 | 0x24 | R
37 | 0x25 | R
38 | 0x26 | R | LEDs_H | 1x | LED INFORMATIONS UPPER 16 BIT (Polls)
[5 empty] | BIT_0= Common Signal in any Failure caused to INV OFF | YES | YES | YES | YES | YES
[5 empty] | BIT_1= There is no critical alarm (if it is 0, yellow alarm level) | YES | YES | YES | YES | YES
[5 empty] | BIT_2= Power supply is ok | YES | YES | YES | YES | YES
[5 empty] | BIT_3= Synchronization To Bypass Lost | YES | YES | YES | YES | YES
BIT_4= No data
BIT_5= No data
BIT_6= No data
BIT_7= No data
[5 empty] | BIT_8= AC Rectifier Input OK | NO | NO | YES | YES | YES
BIT_9= No data
BIT_10= No data
BIT_11= No data
BIT_12= No data
BIT_13= No data
BIT_14= No data
[5 empty] | BIT_15= Battery circuit breaker OFF | NO | NO | YES | YES | YES
39 | 0x27 | R | LEDs_L | 1x | LED INFORMATIONS LOWER 16 BIT (Polls)
[5 empty] | BIT_0= Load is feeding from Battery, Rectfier has no operation | NO | NO | YES | YES | YES
[5 empty] | BIT_1= Load on Inverter | YES | YES | YES | YES | YES
[5 empty] | BIT_2= Bypass Input is OK | YES | YES | YES | YES | YES
[5 empty] | BIT_3= Load on Bypass | YES | YES | YES | YES | YES
[5 empty] | BIT_4= Bypass circuit breaker OFF | YES | YES | YES | YES | YES
[5 empty] | BIT_5= AC Input circuit breaker OFF | NO | NO | YES | YES | YES
[5 empty] | BIT_6= Bypass is Out of Acceptable Limit | YES | YES | YES | YES | YES
[5 empty] | BIT_7= DC Bus Out of limit for inverter operation | YES | YES | YES | YES | YES
[5 empty] | BIT_8= Fan failure detected before 1.5 minute Overtemp Fail | YES | YES | YES | YES | YES
[5 empty] | BIT_9= IGBT saturation or Failure detected | YES | YES | YES | YES | YES
[5 empty] | BIT_10= Overload Occured on Output | YES | YES | YES | YES | YES
[5 empty] | BIT_11= Output Breaker OFF | YES | YES | YES | YES | YES
[5 empty] | BIT_12= Common Signal in any Failure caused to INV OFF | YES | YES | YES | YES | YES
[5 empty] | BIT_13= Over temperature (70C termostat activated) | YES | YES | YES | YES | YES
[5 empty] | BIT_14= Maintanence swich is activated | YES | YES | YES | YES | YES
[5 empty] | BIT_15= Inverter output has long deviation | YES | YES | YES | YES | YES
40 | 0x28 | R | V_inv_L2 | 10x | Inverter Voltage on L2 Phase | YES | YES | YES | YES | YES
41 | 0x29 | R | V_inv_L3 | 10x | Inverter Voltage on L3 Phase | YES | YES | YES | YES | YES
42 | 0x2a | R | V_line13 | 10x | GRID Line Voltage between L13 Phase | NO | NO | YES | YES | YES
43 | 0x2b | R | V_line23 | 10x | GRID Line Voltage between L23 Phase | NO | NO | YES | YES | YES
44 | 0x2c | R | I_out_L2 | 10x | Output Current on L2 Phase (Bypass or INV) | YES | YES | YES | YES | YES
45 | 0x2d | R | I_out_L3 | 10x | Output Current on L3 Phase (Bypass or INV) | YES | YES | YES | YES | YES
46 | 0x2e | R | I_rec_L2 | 10x | Rectifier Input Current on L2 Phase | NO | NO | YES | YES | YES
47 | 0x2f | R | I_rec_L3 | 10x | Rectifier Input Current on L3 Phase | NO | NO | YES | YES | YES
48 | 0x30 | R | F_line | 10x | GRID Line Voltage Frequency | NO | NO | YES | YES | YES
49 | 0x31 | R | F_inv | 10x | Inverter Output Frequency | YES | YES | YES | YES | YES
50 | 0x32 | R | set_T_HT_NM | 1x | event history total event number | YES | YES | YES | YES | YES
51 | 0x33 | R | set_HT_NM_BUS | 1x | Currently displayed event number from event history | YES | YES | YES | YES | YES
52 | 0x34 | R | htadres | 1x | currently displayed event code, check from event code table | YES | YES | YES | YES | YES
53 | 0x35 | R | htadres+1 | 1x | currently displayed event value, check from event code table | YES | YES | YES | YES | YES
54 | 0x36 | R | htadres+2 | 1x | reading currently displayed event’s DAY | YES | YES | YES | YES | YES
55 | 0x37 | R | htadres+3 | 1x | reading currently displayed event’s MONTH | YES | YES | YES | YES | YES
56 | 0x38 | R | htadres+4 | 1x | reading currently displayed event’s HOUR | YES | YES | YES | YES | YES
57 | 0x39 | R | htadres+5 | 1x | reading currently displayed event’s MINUTE | YES | YES | YES | YES | YES
58 | 0x3a | R | htadres+6 | 1x | reading currently displayed event’s SECOND | YES | YES | YES | YES | YES
59 | 0x3b | R | RELAY8 | 1x | readi 8 dry contac RELAYS current position | YES | YES | YES | YES | YES
60 | 0x3c | R / WR | set_Vline12_par | 10x | Line voltage calibration parameter for L12 | NO | NO | YES | YES | YES
61 | 0x3d | R / WR | set_Iline1_par | 10x | Line current calibration parameter for L1 | NO | NO | YES | YES | YES
62 | 0x3e | R / WR | set_Vrec_par | 10x | BATTERY DC voltage calibration parameter | NO | NO | YES | YES | YES
63 | 0x3f | R / WR | set_Tint_par | 10x | Internal temperature calibration parameter for rectifier | NO | NO | YES | YES | YES
64 | 0x40
65 | 0x41 | R / WR | set_Ibat_par | 10x | Battery current calibration parameter | NO | NO | YES | YES | YES
66 | 0x42 | R / WR
67 | 0x43 | R / WR
68 | 0x44 | R / WR | set_Iline2_par | 10x | Rectifier Line current calibration parameter for L2 | NO | NO | YES | YES | YES
69 | 0x45 | R / WR | set_Iline2_par | 10x | Rectifier Line current calibration parameter for L3 | NO | NO | YES | YES | YES
70 | 0x46 | R / WR | set_RELAY1_LED | 10x | dry contact 1 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
71 | 0x47 | R / WR |  | 10x | dry contact 1 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
72 | 0x48 | R / WR | set_RELAY2_LED | 10x | dry contact 2 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
73 | 0x49 | R / WR |  | 10x | dry contact 2 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
74 | 0x4a | R / WR | set_RELAY3_LED | 10x | dry contact 3 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
75 | 0x4b | R / WR |  | 10x | dry contact 3 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
76 | 0x4c | R / WR | set_RELAY4_LED | 10x | dry contact 4 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
77 | 0x4d | R / WR |  | 10x | dry contact 4 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
78 | 0x4e | R / WR | set_RELAY5_LED | 10x | dry contact 5 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
79 | 0x4f | R / WR |  | 10x | dry contact 5 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
80 | 0x50 | R / WR | set_RELAY6_LED | 10x | dry contact 6 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
81 | 0x51 | R / WR |  | 10x | dry contact 6 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
82 | 0x52 | R / WR | set_RELAY7_LED | 10x | dry contact 7 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
83 | 0x53 | R / WR |  | 10x | dry contact 7 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
84 | 0x54 | R / WR | set_RELAY8_LED | 10x | dry contact 8 LED, selection code upper word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
85 | 0x55 | R / WR |  | 10x | dry contact 8 LED, selection code lower word (Look LEDs 32 bit) | YES | YES | YES | YES | YES
86 | 0x56 | R / WR
87 | 0x57 | R / WR
88 | 0x58 | R / WR
89 | 0x59 | R / WR
90 | 0x5a | R / WR
91 | 0x5b | R / WR
92 | 0x5c | R / WR
93 | 0x5d | R / WR
94 | 0x5e | R / WR
95 | 0x5f | R / WR | set_Vline13_par | 10x | Line voltage calibration parameter for L13 | NO | NO | YES | YES | YES
96 | 0x60 | R / WR | set_Vline23_par | 10x | Line voltage calibration parameter for L23 | NO | NO | YES | YES | YES
97 | 0x61 | R / WR
98 | 0x62 | R / WR
99 | 0x63 | R / WR
100 | 0x64 | R / WR
101 | 0x65 | R / WR | set_BYP_par | 10x | Bypass voltage calibration parameter for L1 | YES | YES | YES | YES | YES
102 | 0x66 | R / WR | set_BYP_par2 | 10x | Bypass voltage calibration parameter for L2 | YES | YES | YES | YES | YES
103 | 0x67 | R / WR | set_BYP_par3 | 10x | Bypass voltage calibration parameter for L3 | YES | YES | YES | YES | YES
104 | 0x68 | R / WR | set_INV_par | 10x | Inverter voltage calibration parameter for L1 | YES | YES | YES | YES | YES
105 | 0x69 | R / WR | set_INV_par2 | 10x | Inverter voltage calibration parameter for L2 | YES | YES | YES | YES | YES
106 | 0x6a | R / WR | set_INV_par3 | 10x | Inverter voltage calibration parameter for L3 | YES | YES | YES | YES | YES
107 | 0x6b | R / WR
108 | 0x6c | R / WR
109 | 0x6d | R / WR
110 | 0x6e | R / WR | set_Iout_par | 10x | Output Current on L1 Phase calibration parameter | YES | YES | YES | YES | YES
111 | 0x6f | R / WR | set_Iout_par2 | 10x | Output Current on L2 Phase calibration parameter | YES | YES | YES | YES | YES
112 | 0x70 | R / WR | set_Iout_par3 | 10x | Output Current on L3 Phase calibration parameter | YES | YES | YES | YES | YES
113 | 0x71 | R / WR | set_Vbus_par | 10x | INV DC bus voltage calibration parameter | YES | YES | YES | YES | YES