## Sheet1
DECIMAL | HEX | READABLE / | DATA | COEFF. | DEFINITION
ADDRESS | ADDRESS | WRITABLE
0 | 0x00 | R / WR | set_V_FLOAT | 10x | battery float charge voltage
1 | 0x01 | R / WR | set_V_BOOST | 10x | battery float charge voltage
2 | 0x02 | R / WR | set_V_LOWBAT | 10x | low battery voltage level
3 | 0x03 | R / WR | set_EQ_BOOST | 10x | battery equalize boost charge voltage
4 | 0x04 | R / WR | set_END_BATTERY_LEVEL | 10x | battery ending voltage level
5 | 0x05 | R / WR | set_I_FLOAT | 10x | return to float from auto boost current level
6 | 0x06 | R / WR | set_I_BOOST | 10x | current level to go auto boost
7 | 0x07 | R / WR | set_I_BAT | 10x | battery current limit
8 | 0x08 | R / WR | set_I_OUT | 10x | rectifier output current limit
9 | 0x09 | R / WR | set_MODE_SWITCH (1,2,3,4,5) | 1x | 1=auto boost, 2=float, 3=manual, 4=equalize, 5=slave
10 | 0x0a | R / WR | set_MAN_BOOST_TIME_HR | 10x | manual boost duration in hours
11 | 0x0b | R / WR | set_BAT_TEST_SWITCH (1,2,3) | 1x | batt. test condition 1=auto, 2=closed,3=manual
12 | 0x0c | R / WR | set_DISCHARGE CURRENT | 1x | discharge current during battery test
13 | 0x0d | R / WR | set_AUTO_BAT_TEST_TIME_HR | x10 | auto battery test period in hours
14 | 0x0e | R / WR | set_DISCHARGE TIME MINUTE | 1x | min. discharge time in hours during battery test
15 | 0x0f | R / WR | set_RECTIFIER (ON / OFF) (0-1) | 1x | rectifier on/off switch 0=off, 1=on
16 | 0x10 | R / WR | set_EVENT NUMBER | 1x | reading event number from event history
17 | 0x11 | R / WR |  | 10x
18 | 0x12 | R / WR |  | 10x
19 | 0x13 | R / WR
20 | 0x14 | R / WR | set_DAY / DATE | 1x | day of DATE
21 | 0x15 | R / WR | set_MONTH / DATE | 1x | month of DATE
22 | 0x16 | R / WR | set_YEAR / DATE | 1x | year of DATE
23 | 0x17 | R / WR | set_HOUR / DATE | 1x | hour of TIME
24 | 0x18 | R / WR | set_MINUTE / DATE | 1x | minute of TIME
25 | 0x19 | R | FREQ. | 10x | line frequency
26 | 0x1a | R | V_LINE1 | 10x | line voltage 1
27 | 0x1b | R | V_LINE2 | 10x | line voltage 2
28 | 0x1c | R | V_LINE3 | 10x | line voltage 3
29 | 0x1d | R | I_LINE1 | 10x | line current 1
30 | 0x1e | R | I_LINE2 | 10x | line current 2
31 | 0x1f | R | I_LINE3 | 10x | line current 3
32 | 0x20 | R | V_BAT | 10x | battery output voltage
33 | 0x21 | R | I_BAT (signed int16) | 10x | battery output current (signed int16)
34 | 0x22 | R | V_LOAD | 10x | load output voltage
35 | 0x23 | R | I_LOAD | 10x | load output current
36 | 0x24 | R | d | 1x
37 | 0x25 | R | RELAY OUTPUTS | 1x | programmed 8 dry contacts positions
38 | 0x26 | R | LED_high16 | 1x | MONITORRING LEDS
BIT_0= Rectifier operation fail
BIT_1= There is no critical alarm
BIT_2= Power supply is ok
BIT_3= Charger in equalize mode
BIT_4= Charger in current mode
BIT_5= Charger in boost mode
BIT_6= Charger in float mode
BIT_7= Line is out of limit
BIT_8= No data
BIT_9= No data
BIT_10= No data
BIT_11= No data
BIT_12= No data
BIT_13= No data
BIT_14= No data
BIT_15= No data
39 | 0x27 | R | LEDS_low16 | 1x | MONITORRING LEDS
BIT_0= Battery circuit breaker open
BIT_1= Load circuit breaker open
BIT_2= No data
BIT_3= No data
BIT_4= Line circuit breaker open
BIT_5= Battery test fail
BIT_6= Low battery
BIT_7= Battery ending
BIT_8= Fan failure
BIT_9= Earth Leakage (+)
BIT_10= Earth Leakage (-)
BIT_11= No data
BIT_12= Common Failure
BIT_13= Over temperature
BIT_14= Rectifier output under voltage
BIT_15= Rectifier output over voltage
40 | 0x28 | R | Internal Temperature | 10x | Internal Temperature degree in celsius
41 | 0x29
42 | 0x2a
43 | 0x2b
44 | 0x2c
45 | 0x2d
46 | 0x2e
47 | 0x2f
48 | 0x30
49 | 0x31
50 | 0x32 | R | TOTAL EVENT NUMBER | 1x | event history total event number
51 | 0x33 | R | EVENT NUMBER to READ | 1x | reading event number from event history
52 | 0x34 | R | EVENT CODE of EVENT | 1x | event code, check from event code table
53 | 0x35 | R | EVENT VALUE of EVENT | 1x | event value, check from event code table
54 | 0x36 | R | DAY of EVENT | 1x | reading event’s DAY
55 | 0x37 | R | MONTH of EVENT | 1x | reading event’s MONTH
56 | 0x38 | R | HOUR of EVENT | 1x | reading event’s HOUR
57 | 0x39 | R | MINUTE of EVENT | 1x | reading event’s MINUTE
58 | 0x3a | R | SECOND of EVENT | 1x | reading event’s SECOND
59 | 0x3b
60 | 0x3c | R / WR | set_V_LINE1_parameter | 10x | Line voltage calibration parameter
61 | 0x3d | R / WR | set_I_LINE1_ parameter | 10x | Line current calibration parameter
62 | 0x3e | R / WR | set_V_BAT_ parameter | 10x | BATTERY DC voltage calibration parameter
63 | 0x3f | R / WR | set_T_ parameter | 10x | Internal temperature calibration parameter
64 | 0x40
65 | 0x41 | R / WR | set_I_LOAD_parameter | 10x | LOAD DC current calibration parameter
66 | 0x42 | R / WR | set_I_BAT_parameter | 10x | BATTERY DC current calibration parameter
67 | 0x43 | R / WR | set_V_LOAD_ parameter | 10x | LOAD DC voltage calibration parameter
68 | 0x44 | R / WR | set_I_LINE2_ parameter | 10x | Line current calibration parameter
69 | 0x45 | R / WR | set_I_LINE3_ parameter | 10x | Line current calibration parameter
70 | 0x46 | R / WR | set_Relay1_high16 | 1x | dry contact selection code upper word
71 | 0x47 | R / WR | set_Relay1_low16 | 1x | dry contact selection code lower word
72 | 0x48 | R / WR | set_Relay2_high16 | 1x | dry contact selection code upper word
73 | 0x49 | R / WR | set_Relay2_low16 | 1x | dry contact selection code lower word
74 | 0x4a | R / WR | set_Relay3_high16 | 1x | dry contact selection code upper word
75 | 0x4b | R / WR | set_Relay3_low16 | 1x | dry contact selection code lower word
76 | 0x4c | R / WR | set_Relay4_high16 | 1x | dry contact selection code upper word
77 | 0x4d | R / WR | set_Relay4_low16 | 1x | dry contact selection code lower word
78 | 0x4e | R / WR | set_Relay5_high16 | 1x | dry contact selection code upper word
79 | 0x4f | R / WR | set_Relay5_low16 | 1x | dry contact selection code lower word
80 | 0x50 | R / WR | set_Relay6_high16 | 1x | dry contact selection code upper word
81 | 0x51 | R / WR | set_Relay6_low16 | 1x | dry contact selection code lower word
82 | 0x52 | R / WR | set_Relay7_high16 | 1x | dry contact selection code upper word
83 | 0x53 | R / WR | set_Relay7_low16 | 1x | dry contact selection code lower word
84 | 0x54 | R / WR | set_Relay8_high16 | 1x | dry contact selection code upper word
85 | 0x55 | R / WR | set_Relay8_low16 | 1x | dry contact selection code lower word
86 | 0x56 | R / WR | relay1_on_time | 1x | not_used in this version
87 | 0x57 | R / WR | relay2_on_time | 1x | not_used in this version
88 | 0x58 | R / WR | relay3_on_time | 1x | not_used in this version
89 | 0x59 | R / WR | relay4_on_time | 1x | not_used in this version
90 | 0x5a | R / WR | relay5_on_time | 1x | not_used in this version
91 | 0x5b | R / WR | relay6_on_time | 1x | not_used in this version
92 | 0x5c | R / WR | relay7_on_time | 1x | not_used in this version
93 | 0x5d | R / WR | relay8_on_time | 1x | not_used in this version
94 | 0x5e
95 | 0x5f | R / WR | set_V_LINE2_parameter | 10x | Line voltage calibration parameter
96 | 0x60 | R / WR | set_V_LINE3_parameter | 10x | Line voltage calibration parameter
97 | 0x61